## Slide 1: Electrical Transmission System
In last lecture we have discussed the potential distribution over string insulator in detail. In this lecture we will study about Corona in transmission lines, factor affecting corona and its pros and cons.

## Slide 2
Corona
When an alternating potential difference is applied across two conductors whose spacing is large as compared to their diameters, there is no apparent change in the condition of atmospheric air surrounding the wires if the applied voltage is low.
However, when the applied voltage exceeds a certain value, called critical disruptive voltage, the conductors are surrounded by a faint violet glow called corona.

## Slide 3
The phenomenon of corona is accompanied by a hissing sound, production of ozone, power loss and radio interference.
The higher the voltage is raised, the larger and higher the luminous envelope becomes, and greater are the sound, the power loss and the radio noise.
If the applied voltage is increased to breakdown value, a flash-over will occur between the conductors due to the breakdown of air insulation.

## Slide 4
The phenomenon of violet glow, hissing noise and production of ozone gas in an overhead transmission line is known as corona.

## Slide 5
If the conductors are polished and smooth, the corona glow will be uniform throughout the length of the conductors, otherwise the rough points will appear brighter.
With d.c. voltage, there is difference in the appearance of the two wires.
The positive wire has uniform glow about it, while the negative conductor has spotty glow.

## Slide 6
Factors Affecting Corona
The phenomenon of corona is affected by the physical state of the atmosphere as well as by the conditions of the line. The following are the factors upon which corona depends :

## Slide 7
Atmosphere
As corona is formed due to ionization of air surrounding the conductors, therefore, it is affected by the physical state of atmosphere.
In the stormy weather, the number of ions is more than normal and as such corona occurs at much less voltage as compared with fair weather.

## Slide 8
(ii) Conductor size.
The corona effect depends upon the shape and conditions of the conductors.
The rough and irregular surface will give rise to more corona because unevenness of the surface decreases the value of breakdown voltage.
Thus a stranded conductor has irregular surface and hence gives rise to more corona that a solid conductor.

## Slide 9
(iii) Spacing between conductors.
If the spacing between the conductors is made very large as compared to their diameters, there may not be any corona effect.
It is because larger distance between conductors reduces the electro-static stresses at the conductor surface, thus avoiding corona formation.

## Slide 10
(iv) Line voltage.
The line voltage greatly affects corona. If it is low, there is no change in the condition of air surrounding the conductors and hence no corona is formed.
However, if the line voltage has such a value that electrostatic stresses developed at the conductor surface make the air around the conductor conducting, then corona is formed.

## Slide 11
Important Terms
The phenomenon of corona plays an important role in the design of an overhead transmission line. Therefore, it is profitable to consider the following terms much used in the analysis of corona effects:
Critical disruptive voltage.
It is the minimum phase-neutral voltage at which corona occurs.

## Slide 12
(ii) Visual critical voltage.
It is the minimum phase-neutral voltage at which corona glow appears all along the line conductors.

## Slide 13
(iii) Power loss due to corona.
Formation of corona is always accompanied by energy loss which is dissipated in the form of light, heat, sound and chemical action.
When disruptive voltage is exceeded, the power loss due to corona is given by :

## Slide 14
Advantages and Disadvantages of Corona
Corona has many advantages and disadvantages. In the correct design of a high voltage overhead line, a balance should be struck between the advantages and disadvantages.
Advantages
Due to corona formation, the air surrounding the conductor becomes conducting and hence virtual diameter of the conductor is increased. The increased diameter reduces the electrostatic stresses between the conductors.
Corona reduces the effects of transients produced by surges.

## Slide 15
Disadvantages
Corona is accompanied by a loss of energy. This affects the transmission efficiency of the line.
Ozone is produced by corona and may cause corrosion of the conductor due to chemical action.
The current drawn by the line due to corona is non-sinusoidal and hence non-sinusoidal voltage drop occurs in the line. This may cause inductive interference with neighbouring communication lines.

## Slide 16
Methods of Reducing Corona Effect
It has been seen that intense corona effects are observed at a working voltage of 33 kV or above. Therefore, careful design should be made to avoid corona on the sub-stations or bus-bars rated for 33 kV and higher voltages otherwise highly ionized air may cause flash-over in the insulators or between the phases, causing considerable damage to the equipment. The corona effects can be reduced by the
following methods :

## Slide 17
By increasing conductor size.
By increasing conductor size, the voltage at which corona occurs is raised and hence corona effects are considerably reduced.
This is one of the reasons that ACSR conductors which have a larger cross-sectional area are used in transmission lines.

## Slide 18
By increasing conductor spacing.
By increasing the spacing between conductors, the voltage at which corona occurs is raised and hence corona effects can be eliminated.
However, spacing cannot be increased too much otherwise the cost of supporting structure (e.g., bigger cross arms and supports) may increase to a considerable extent.

## Slide 19
Example. A 3-phase line has conductors 2 cm in diameter spaced equilaterally 1 m apart. If the dielectric strength of air is 30 kV (max) per cm, find the disruptive critical voltage for the line. Take air density factor δ = 0·952 and irregularity factor mo = 0·9.

## Slide 20
References
Principles of Power Systems by V.K Mehta